## 28th February
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 28th February 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 630.352 | 618.3 |  |  | 1.039 | 3.15 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 11429.32 | 11210.4 |  |  | 20.3676 | 85.9 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  | 7.7
Year | 24131.15 | 23672.3 |  |  | 40.8351 | 184.2 |  |  |  |  | 215 |  | 0.08961 | 0.8 |  | 19.21 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(February) | 94.77 |  | 85
[15 empty] | 3 Month(October 24-December 24) | 98.15 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(August 24 -December 24) | 94.97 |  | 85
Day | 0.779 | 0 | 0 | 122.22 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 96.15 |  | 85
Month | 17.86 | 0 | 0 | 2296.08 | 0 |  | Month |  |  |  | 8 |  | 94.77
Year | 37.43 | 0 | 0 | 4820.24 | 2.11 |  | Year | 40263.08 |  |  | 16 |  | 96.15
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | DG#3 low stat air pressure. | [7 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | DG#4 low strat air pressure
1970-01-01 03:01 | 1970-01-01 03:01 | DG5 | [5 empty] | DG#5 low start air presure | [6 empty] | Initial | 4848.78 |  | 30.87 |  | 20.67 |  |  |  | Day
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | low start air presure | [6 empty] | Input | 0 |  |  |  | 0 |  |  |  | Month | 3
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | low start air presure | [6 empty] | Consumption | [8 empty] | Year | 3
1970-01-01 03:01 | 1970-01-01 03:01 | DG5 | [5 empty] | low start air presure | [6 empty] | Final | 4726.57 |  | 30.09 |  | 20.67
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | low start air presure | [15 empty] | EXTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | low start air presure | [7 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
1970-01-01 03:01 | 1970-01-01 03:01 | DG5 | [5 empty] | low start air presure | [8 empty] | % | 13 |  | % | 3 |  |  | Day
1970-01-01 03:01 | 1970-01-01 03:01 | DG1 | [5 empty] | DG#1 trips with damper missmatch | [15 empty] | Month | 1
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | DG#3 start failure | [15 empty] | Year | 1
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | DG#3 start failure | [7 empty] | FUEL LIQUIDATED DAMAGES
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | DG#4 trips with damper missmatch | [7 empty] | Day |  | 0 | [6 empty] | 1=
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | DG#4 trips with low lube oil pressure | [7 empty] | Month |  | 559.72
1970-01-01 03:01 | 1970-01-01 03:01 | DG1 | [5 empty] | DG#1 Power supply failure -EAP | [7 empty] | Year |  | 559.72
1970-01-01 03:01 | 1970-01-01 03:01 | DG1 | [5 empty] | DG#1 Power supply failure -EAP

## 1st March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 1st March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 314.296 | 308.2 |  |  | 0.8229 | 3.76 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 314.296 | 308.2 |  |  | 0.8229 | 3.76 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  | 7.7
Year | 24445.45 | 23980.5 |  |  | 41.6576 | 188.12 |  |  |  |  | 215 |  | 0.0884 | 0.8 |  | 17.73 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 0.15 | 0 | 0 | 64.75 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.44 |  | 85
Month | 0.15 | 0 | 0 | 64.75 | 0 |  | Month |  |  |  | 0 |  | 100
Year | 37.57 | 0 | 0 | 4884.99 | 2.11 |  | Year | 40263.08 |  |  | 16 |  | 97.44
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
[16 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4726.57 |  | 30.09 |  | 20.67 |  |  |  | Day
[15 empty] | Input | 0 |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4661.82 |  | 29.94 |  | 20.67
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 13 |  | % | 3 |  |  | Day
Month
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 2nd March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 2nd March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 222.52 | 217.7 |  |  | 0.452 | 3.36 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 536.816 | 525.9 |  |  | 1.2752 | 7.12 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  | 7.7
Year | 24667.972 | 24198.2 |  |  | 42.1096 | 191.48 |  |  |  |  | 215 |  | 0.0884 | 0.8 |  | 17.01 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 0.39 | 0 | 0 | 44.17 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.44 |  | 85
Month | 0.53 | 0 | 0 | 108.92 | 0 |  | Month |  |  |  | 0 |  | 100
Year | 37.96 | 0 | 0 | 4929.16 | 2.11 |  | Year | 40263.08 |  |  | 16 |  | 97.44
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
[16 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4661.82 |  | 29.94 |  | 20.67 |  |  |  | Day
[15 empty] | Input | 0 |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4617.65 |  | 29.55 |  | 20.67
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 13 |  | % | 3 |  |  | Day
[24 empty] | Month | 1
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 3rd March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 3rd March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 317.44 | 311.7 |  |  | 0.704 | 3.01 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 854.256 | 837.6 |  |  | 1.979 | 10.13 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  | 7.7
Year | 24985.412 | 24509.9 |  |  | 42.8134 | 194.49 |  |  |  |  | 215 |  | 0.08647 | 0.8 |  | 17.27 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 0.92 | 0 | 0 | 65.61 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.44 |  | 85
Month | 1.46 | 0 | 0 | 174.53 | 0 |  | Month |  |  |  | 0 |  | 100
Year | 38.88 | 0 | 0 | 4994.78 | 2.11 |  | Year | 40263.08 |  |  | 16 |  | 97.44
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
[16 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4617.6455 |  | 29.55 |  | 20.67 |  |  |  | Day
[15 empty] | Input | 195.66 |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4747.6927 |  | 28.6286 |  | 20.67
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 13 |  | % | 3 |  |  | Day
[24 empty] | Month | 1
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 4th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 4th March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 351.32 | 345.3 |  |  | 0.519 | 2.98 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 1205.576 | 1182.9 |  |  | 2.498 | 13.11 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  | 7.7
Year | 25336.73 | 24855.2 |  |  | 43.3328 | 197.47 |  |  |  |  | 215 |  | 0.08524 | 0.8 |  | 17.53 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 0.44 | 0 | 0 | 72.08 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.44 |  | 85
Month | 1.895 | 0 | 0 | 246.62 | 0 |  | Month |  |  |  | 0 |  | 100
Year | 39.32 | 0 | 0 | 5066.86 | 2.11 |  | Year | 40263.08 |  |  | 16 |  | 97.44
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | plant | [5 empty] | Plant trip due to grid spike (undervoltage) NCC Oriare | [7 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4747.6927 |  | 28.6286 |  | 20.67 |  |  |  | Day
[15 empty] | Input | 83.82 |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4759.4297 |  | 28.1918 |  | 20.67
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 13 |  | % | 3 |  |  | Day
[24 empty] | Month | 1
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 5th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 5th March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 469.676 | 460.9 |  |  | 0.506 | 2.8 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 1675.252 | 1643.8 |  |  | 3.004 | 15.91 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  | 7.7
Year | 25806.41 | 25316.1 |  |  | 43.8385 | 200.27 |  |  |  |  | 215 |  | 0.084 | 0.8 |  | 18.06 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 0.63 | 0 | 0 | 92.25 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.44 |  | 85
Month | 2.53 | 0 | 0 | 338.86 | 0 |  | Month |  |  |  | 0 |  | 100
Year | 39.95 | 0 | 0 | 5159.11 | 2.11 |  | Year | 40263.08 |  |  | 16 |  | 97.44
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | plant | [5 empty] | Plant trip due to grid spike (undervoltage) NCC Oriare | [7 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4759.4297 |  | 28.1918 |  | 20.67 |  |  |  | Day
[15 empty] | Input | 83.66 |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4750.84 |  | 27.56 |  | 20.67
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 13 |  | % | 3 |  |  | Day
[24 empty] | Month | 1
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 6th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 6th March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 425.808 | 418.4 |  |  | 0.918 | 3.61 |  |  |  |  | 215 |  | 3.3094 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 2101.06 | 2062.2 |  |  | 3.921 | 19.52 |  |  |  |  | 215 |  | 3.3094 | 0.8 |  |  | 15 |  | 7.7
Year | 26232.22 | 25734.5 |  |  | 44.756 | 203.88 |  |  |  |  | 215 |  | 0.35263 | 0.8 |  | 18.3 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 0.53 | 0 | 0 | 83.95 | 6.85 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.43 |  | 85
Month | 3.06 | 0 | 0 | 422.81 | 6.85 |  | Month |  |  |  | 0 |  | 100
Year | 40.48 | 0 | 0 | 5243.06 | 8.96 |  | Year | 40263.08 |  |  | 16 |  | 97.43
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | plant | [5 empty] | Plant trip due to grid spike (undervoltage) NCC Oriare | [7 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4750.84 |  | 27.56 |  | 20.67 |  |  |  | Day
[15 empty] | Input | 111.42 |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4778.31 |  | 27.03 |  | 13.8219
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 41 |  | % | 16 |  |  | Day
[24 empty] | Month | 1
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 7th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 7th March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 358.752 | 352.5 |  |  | 0.688 | 3.091 |  |  |  |  | 215 |  | 2.823 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 2459.812 | 2414.7 |  |  | 4.61 | 22.61 |  |  |  |  | 215 |  | 2.823 | 0.8 |  |  | 15 |  | 7.7
Year | 26590.972 | 26087 |  |  | 45.44 | 206.97 |  |  |  |  | 215 |  | 0.3446 | 0.8 |  | 18.3 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 1.022 | 0 | 0 | 70.53 | 6.85 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.43 |  | 85
Month | 4.08 | 0 | 0 | 493.34 | 6.85 |  | Month |  |  |  | 0 |  | 100
Year | 41.5 | 0 | 0 | 5313.59 | 8.96 |  | Year | 40263.08 |  |  | 16 |  | 97.43
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | plant | [5 empty] | Plant trip due to grid spike (undervoltage) NCC Oriare | [7 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4778.31 |  | 27.03 |  | 20.67 |  |  |  | Day
[15 empty] | Input | 83.44 |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4791.2236 |  | 26 |  | 13.8219
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 41 |  | % | 16 |  |  | Day
[24 empty] | Month | 1
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 8th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 7th March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | [10 empty] | 215 |  | 2.823 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | [10 empty] | 215 |  | 2.823 | 0.8 |  |  | 15 |  | 7.7
Year | [10 empty] | 215 |  | 0.3428 | 0.8 |  | 18.39 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 0.29 | 0 | 0 | 77.92 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.43 |  | 85
Month | 4.37 | 0 | 0 | 571.26 | 6.85 |  | Month |  |  |  | 0 |  | 100
Year | 41.8 | 0 | 0 | 5391.51 | 8.96 |  | Year | 40263.08 |  |  | 16 |  | 97.43
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | plant | [5 empty] | Plant trip due to grid spike (undervoltage) NCC Oriare | [7 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4791.2236 |  | 26 |  | 20.67 |  |  |  | Day
[15 empty] | Input |  |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4713.3056 |  | 25.7124 |  | 13.8219
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 41 |  | % | 16 |  |  | Day
[24 empty] | Month | 1
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 8th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 28th February 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 630.352 | 618.3 |  |  | 1.039 | 3.15 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 11429.32 | 11210.4 |  |  | 20.3676 | 85.9 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  | 7.7
Year | 24131.15 | 23672.3 |  |  | 40.8351 | 184.2 |  |  |  |  | 215 |  | 0.08961 | 0.8 |  | 19.21 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(February) | 94.77 |  | 85
[15 empty] | 3 Month(October 24-December 24) | 98.15 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(August 24 -December 24) | 94.97 |  | 85
Day | 0.779 | 0 | 0 | 122.22 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 96.15 |  | 85
Month | 17.86 | 0 | 0 | 2296.08 | 0 |  | Month |  |  |  | 8 |  | 94.77
Year | 37.43 | 0 | 0 | 4820.24 | 2.11 |  | Year | 40263.08 |  |  | 16 |  | 96.15
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | DG#3 low stat air pressure. | [7 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | DG#4 low strat air pressure
1970-01-01 03:01 | 1970-01-01 03:01 | DG5 | [5 empty] | DG#5 low start air presure | [6 empty] | Initial | 4848.78 |  | 30.87 |  | 20.67 |  |  |  | Day
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | low start air presure | [6 empty] | Input | 0 |  |  |  | 0 |  |  |  | Month | 3
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | low start air presure | [6 empty] | Consumption | [8 empty] | Year | 3
1970-01-01 03:01 | 1970-01-01 03:01 | DG5 | [5 empty] | low start air presure | [6 empty] | Final | 4726.57 |  | 30.09 |  | 20.67
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | low start air presure | [15 empty] | EXTERNAL TRIPS
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | low start air presure | [7 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
1970-01-01 03:01 | 1970-01-01 03:01 | DG5 | [5 empty] | low start air presure | [8 empty] | % | 13 |  | % | 3 |  |  | Day
1970-01-01 03:01 | 1970-01-01 03:01 | DG1 | [5 empty] | DG#1 trips with damper missmatch | [15 empty] | Month | 1
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | DG#3 start failure | [15 empty] | Year | 1
1970-01-01 03:01 | 1970-01-01 03:01 | DG3 | [5 empty] | DG#3 start failure | [7 empty] | FUEL LIQUIDATED DAMAGES
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | DG#4 trips with damper missmatch | [7 empty] | Day |  | 0 | [6 empty] | 1=
1970-01-01 03:01 | 1970-01-01 03:01 | DG4 | [5 empty] | DG#4 trips with low lube oil pressure | [7 empty] | Month |  | 559.72
1970-01-01 03:01 | 1970-01-01 03:01 | DG1 | [5 empty] | DG#1 Power supply failure -EAP | [7 empty] | Year |  | 559.72
1970-01-01 03:01 | 1970-01-01 03:01 | DG1 | [5 empty] | DG#1 Power supply failure -EAP

## 9th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 2nd March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 222.52 | 217.7 |  |  | 0.452 | 3.36 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  |  |  |  | 14th Jan 2025 | 87 |  | 88.85 | 87.87
Month | 536.816 | 525.9 |  |  | 1.2752 | 7.12 |  |  |  |  | 215 |  | 0 | 0.8 |  |  | 15 |  | 7.7
Year | 24667.972 | 24198.2 |  |  | 42.1096 | 191.48 |  |  |  |  | 215 |  | 0.0884 | 0.8 |  | 17.01 | 15 |  | 11.4 | 9.53
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
[15 empty] | 1 Month(March) | 100 |  | 85
[15 empty] | 3 Month(December 24-February 25) | 96.5 |  | 85
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25) | 97.76 |  | 85
Day | 0.39 | 0 | 0 | 44.17 | 0 |  | Day | 0 |  |  | 0 |  | 100 |  | Annual | 97.44 |  | 85
Month | 0.53 | 0 | 0 | 108.92 | 0 |  | Month |  |  |  | 0 |  | 100
Year | 37.96 | 0 | 0 | 4929.16 | 2.11 |  | Year | 40263.08 |  |  | 16 |  | 97.44
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
[16 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | 4661.82 |  | 29.94 |  | 20.67 |  |  |  | Day
[15 empty] | Input | 0 |  |  |  | 0 |  |  |  | Month
[15 empty] | Consumption | [8 empty] | Year | 3
[15 empty] | Final | 4617.65 |  | 29.55 |  | 20.67
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % | 13 |  | % | 3 |  |  | Day
[24 empty] | Month | 1
[24 empty] | Year | 1
FUEL LIQUIDATED DAMAGES
[16 empty] | Day |  | 0 | [6 empty] | 1=
Month
[16 empty] | Year |  | 559.72

## 10th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 2nd March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | [21 empty] | 14th Jan 2025
Month
Year
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
1 Month(March)
3 Month(December 24-February 25)
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25)
Day | [6 empty] | Day | [7 empty] | Annual
Month | [6 empty] | Month
Year | [6 empty] | Year
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
[16 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | [8 empty] | Day
[15 empty] | Input | [8 empty] | Month
[15 empty] | Consumption | [8 empty] | Year
Final
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % |  |  | % |  |  |  | Day
Month
Year
FUEL LIQUIDATED DAMAGES
[16 empty] | Day | [8 empty] | 1=
Month
Year

## 13th March
DAILY PRODUCTION REPORT
DOC REF: TPL-OPS-08A | 2nd March 2025
| ENERGY BALANCE | [7 empty] | SFOC (HFO+AGO) |  |  |  | SLOC |  |  | UTILIZATION FACTOR | [5 empty] | CAPACITY TEST (MW)
| Gross Energy | Net Energy | Auxiliary Consumption |  | Solar PV Energy | Received Energy (back feed) | Total Auxilliary consumption | Solar PV Contribution | Real(Net Energy) HFO+DO | Real(Net Energy) HFO | PPA | Deviation | Real | PPA | Deviation | Real 2025 | Budget | Deviation | Year-a-head notification (2025) | Real 2024 |  | DATE | PPA |  | Actual 2025 | Actual 2024
| MWh | MWh | MWh | % | MWh | MWh | MWh | % | g/KWh |  |  | % | g/KWh |  | % | % | [6 empty] | MW |  |  | MW
Day | 599.988 | [20 empty] | 14th Jan 2025
Month
Year
[8 empty] | AVAILABILITY | [7 empty] | PPA AVAILABILITY
| GAS-OIL (AGO) (MT) |  | HFO (MT) |  | LO (MT) |  |  | Unavailable E |  |  | Incidents |  | Availability |  |  | Real
[16 empty] | Real |  | PPA |  | Desv
1 Month(March)
3 Month(December 24-February 25)
| Aux Boiler | Engines | Aux Boiler | Engines | Engines |  |  | MWh |  |  | Number |  | % |  | 5 Month(October 24 -February 25)
Day | [6 empty] | Day | [7 empty] | Annual
Month | [6 empty] | Month
Year | [6 empty] | Year
[15 empty] | STOCK | [8 empty] | TRIPS
Start time | End time | Affected engines |  |  | MWh |  | code | Comment | [6 empty] | FUEL & OIL
[16 empty] | HFO |  | LFO |  | LO |  |  |  | INTERNAL TRIPS
[16 empty] | Ton | % | Ton | % | Ton | % |  |  |  | Actual 2025 | Actual 2024
[15 empty] | Initial | [8 empty] | Day
[15 empty] | Input | [8 empty] | Month
[15 empty] | Consumption | [8 empty] | Year
Final
EXTERNAL TRIPS
[16 empty] | HFO SLUDGE | m3 |  | USED OIL | m3 |  |  |  |  | Actual 2025 | Actual 2024
[17 empty] | % |  |  | % |  |  |  | Day
Month
Year
FUEL LIQUIDATED DAMAGES
[16 empty] | Day | [8 empty] | 1=
Month
Year